## Slide 1: Substation and Distribution Automation
Module 10: Introduction to Micro-Grids

## Slide 2: Module 10 Overview
Part 1: …
Part 2: …
Part 3: …
Part 4: …

## Slide 3: Recommended reading
N. Hatziargyriou et al, “Microgrids” IEEE Power & Energy Magazine, July/August 2007
J. Driesen et al, “Design for distributed energy resources,” IEEE Power & Energy Magazine, May/June 2008
B. Kroposki et al, “Making microgrids work,” IEEE Power & Energy Magazine, May/June 2008
F. Katiraei et al, “Microgrids management,” IEEE Power & Energy Magazine, May/June 2008
C. Marnay et al “Future Roles of Milli-, Micro-, and Nano- Grids,” CIGRÉ International Symposium, Bologna, Italy, September, 2011

## Slide 4: Distributed energy resources (DER)
Microgrids are a framework to address the integration and control of distributed energy resources (DER)
DERs include:
  Small (kW-scale) combined heat and power (CHP)
  Distributed renewable generation: e.g. rooftop photovoltaic panes, small wind turbines, biogas digesters
  Heat and electricity storage
  Controllable loads (demand response): e.g. electric water heaters, HVAC, other controllable appliances

## Slide 5: What are microgrids?
Definition of microgrid1: Group of locally-controlled distributed energy resources (DER) connected to a low voltage (≈ 1 kV) or medium voltage (≈ 1 to 69 kV) distribution network.
  Behaves as a single producer or load
  Can operate in islanded mode
  Small isolated power system also seen as microgrids
Microgrids that can separate from utility grid during disruption and continue to serve critical local load until grid service is restored (main objective of CERTS microgrid)
1: N. Hatziargyriou et al, “Microgrids” IEEE Power & Energy Magazine, July/August 2007

## Slide 6: Why microgrids?
Microgrids is a way to enable benefits of DERs:
  Increase energy efficiency through combined heat and power (CHP)
  Reduce carbon emissions
  Increase local power quality and reliability
  Reduced line losses
  Transmission investment deferral
  Reduce expensive fuel consumption in remote isolated microgrids
Challenge of controlling large number of DER can be addressed by microgrids. Microgrids coordinate DERs in a decentralized way reducing the control burden on the grid.
Enable provision of heterogeneous levels of power quality and reliability (PQR). For example, very high PQR provided to essential services like hospitals and communication equipment, while lower PQR provided to non essential loads like water pumps.

## Slide 7: Consortium for Electricity Reliability Solutions (CERTS) Microgrids
Emphasis on microgrids that can separate from utility grid during disruption and continue to serve critical local load until grid service is restored
< 2MW peak sites,
No need of costly fast electrical controls
  Droop controllers responding to local voltage and frequency
  Single point of common coupling that does not export power (single controlled load)
No single device is essential (robust system)
Design to provide heterogeneous power quality and reliability. Sensitive loads served in island mode during disruption
Generic slow controls, e.g. economic dispatch

## Slide 8: Future role of milligrids, microgrids, and nanogrids
Radical reorganization of parts of the distribution network and customer sites
New proposed entities: community grids or milligrids that operate a segment of the existing distribution system, microgrids which are akin to current customer sites but which have automonous control, and nanogrids, such as telecom or Ethernet networks that currently distribute power to many low-power devices (typically DC with high power quality and reliability).
Local heterogeneous power quality and reliability (PQR) becomes a possibility
C. Marnay et al “Future Roles of Milli-, Micro-, and Nano- Grids,” CIGRÉ International Symposium, Bologna, Italy, September, 2011

## Slide 9: Milligrids, microgrids, and nanogrids
Few large generators
With distributed generation, some small consumers could become producers at some moments (prosumers)
Highly centralized control (traditional paradigm)
Microgrids (or customer microgrid): Independent control nodes. One meter, and one or few points of interconnections
Milligrids (utility microgrid): Sections of distribution network including generation and loads. Public utility regulation
Nanogrids: Low energy grids, typically DC, designed to deliver high PQR
C. Marnay et al “Future Roles of Milli-, Micro-, and Nano- Grids,” CIGRÉ International Symposium, Bologna, Italy, September, 2011

## Slide 10: Enabling heterogeneous power quality and reliability
C. Marnay et al “Future Roles of Milli-, Micro-, and Nano- Grids,” CIGRÉ International Symposium, Bologna, Italy, September, 2011

## Slide 11: Classification of microgrids
Utility Microgrids: Urban and rural
  Objectives: Outage management and renewable integration
  Transition to grid independent or isolated operation: faults, maintenance
Industrial/commercial microgrids: multi- and single-facility
  Objectives: Power quality, reliability and efficiency
  Transition to grid independent or isolated operation: faults, power quality, energy price, maintenance
Remote microgrids
  Objectives: Electrification of remote areas, reduce fuel consumption through renewable integration

## Slide 12: Microgrid components
B. Kroposki et al, “Making microgrids work,” IEEE Power & Energy Magazine, May/June 2008

## Slide 13: Distributed generation
Combined heat and power systems
Photovoltaic generators
Wind turbines
Microturbines
Fuel cells

## Slide 14: Distributed Storage
Community storage (e.g. batteries, flywheels)
Thermal storage

## Slide 15: Demand response
Sensitivity to electricity price
Grid support for stressed condition

## Slide 16: Interconnection switch
Consolidated power switching protective relay metering and communications
Either circuit breaker or semiconductor-based static switches
B. Kroposki et al, “Making microgrids work,” IEEE Power & Energy Magazine, May/June 2008

## Slide 17: Typical topologies
J. Driesen et al, “Design for distributed energy resources,” IEEE Power & Energy Magazine, May/June 2008

## Slide 18: Microgrids typical topologies

## Slide 19: Local electric power system (EPS) island

## Slide 20: Secondary island

## Slide 21: Lateral island

## Slide 22: Circuit island

## Slide 23: Substation bus island

## Slide 24: Substation island

## Slide 25: Adjacent circuit island

## Slide 26: Information exchange

## Slide 27: Stakeholders

## Slide 28: Existing microgrid implementations
USA:
  Dolan technology center (Ohio)
  GE global research microgrid: microgrid energy management (demonstration to end in 2008?)
  Perfect power at the Illinois Institute of Technology
  Military bases: Twentynine Palms Microgrid (GE), Fort Bragg

## Slide 29: Existing microgrid implementations (…cont’d 1)
Europe:
  Kythnos island (Greece)
  Continuon’s MV/LV facility (Netherlands)
  MVV Residential demonstration (Germany)

## Slide 30: Existing microgrid implementations (…cont’d 2)
Japan (motivated by compensation of local variability and present itself as constant load to the grid):
  Aomori (PV, WT, and biogas, biomass, provide electricity and heat, lead acid battery, )
  Aichi (fuel cells, biogas, PV, NaS battery, islanding tests)
  Kyoto (PV, WT, biogas, fuel cells, battery)
  Sendai (demonstrate multiple PQR levels)
  Private sector: Shimizu Corporation, Tokyo Gas

## Slide 31: Existing microgrid implementations (…cont’d 2)
Canada
  Autonomous remote microgrids: Ramea (wind-diesel, 1.2MW peak load, 395kW wind)
  Grid connected: Fortis-Alberta (hydro-wind)
  Planned microgrid islanding: BC Hydro Boston Bar (3MW peak load, 8.64MW run-of-river hydro), Hydro Quebec (15MW load, 31MW steam)

## Slide 32: Sendai, Japan Microgrid
DC loads served directly on a circuit dedicated to critical telecommunications equipment
Multiple qualities of AC services:
  medical school
  high school
  water treatment plant

## Slide 33: AEP / CERTS microgrid test bed
Tested islanding and resynchronization
Electrical protection system distinguished between normal and faulted operation
Controls robust under motor starts and high impedance faults.
R. H. Lasseter et al, “CERTS Microgrid Laboratory Test Bed,” Submitted to IEEE Transactions on Power Delivery, 2010

## Slide 34: AEP / CERTS microgrid test bed

## Slide 35: AEP / CERTS microgrid test bed
J. Eto et al, “CERTS Micorgrid Laboratory Test Bed,” California Energy Commission, Public Interest Energy Research Program. CEC-500-2008-XXX

## Slide 36: AEP / CERTS microgrid test bed
J. Eto et al, “CERTS Micorgrid Laboratory Test Bed,” California Energy Commission, Public Interest Energy Research Program. CEC-500-2008-XXX

## Slide 37: Control of microgrids
Ensure efficient reliable and economic operation and management of microgrids
Control settings and control coordination are different for interconnected mode and islanded mode. Need to adapt
Several levels of control:
  Local control at device level (response to local voltage and frequecy)
  Microgrid central controller (energy efficiency operation optimization)
  Coordination among several microgrids (centralized versus decentralized)

## Slide 38: Microgrid stability
When switching to islanding mode stability becomes an issue.
  Local voltage and frequency controllers should respond appropriately.
  Protection system and settings should be adapted
Stability of isolated microgrid
  Stability of frequency is more challenging in isolated microgrid
  Need to coordinate voltage control
Droop characteristics good option to solve stability problems

## Slide 39: Basic dynamics in isolated microgrid
Generators
Anderson, P. M.; Fouad, A. A. Power System Control and Stability (Second Edition). John Wiley & Sons. 2003.
P. Kundur, Power Systems Stability and Control: McGraw-Hill, Inc., 1994
mechanical
Electrical

## Slide 40: Basic dynamics in isolated microgrid (..cont’d 1)
Motors
Anderson, P. M.; Fouad, A. A. Power System Control and Stability (Second Edition). John Wiley & Sons. 2003.
P. Kundur, Power Systems Stability and Control: McGraw-Hill, Inc., 1994
mechanical
Electrical

## Slide 41: Basic dynamics in isolated microgrid (..cont’d 2)
Network
  Links generators motors and other loads
  Modeling discussed in module 3 “Distribution level power flow”

## Slide 42: Local control at device level: Two or more DERs
Droop control to share load and reactive power control
F. Katiraei et al, “Microgrids management,” IEEE Power & Energy Magazine, May/June 2008

## Slide 43: Power/Energy management objectives
Connected mode:
  Specify DER power output for specific objective (e.g. peak shaving, maximize renewables, minimize fuel costs)
  Consider limitations of DERs
  Main grid to provide difference
  Manage settings of DER in preparation to transition to isolated mode
Isolated mode:
  Power balance to be met by microgrid resources (no main grid contribution)
  Provide power to sensitive loads, use non-sensitive load to help balance the microgrid
  Enable reconnection to main grid after restoration

## Slide 44: Power/energy management
F. Katiraei et al, “Microgrids management,” IEEE Power & Energy Magazine, May/June 2008

## Slide 45: Hierarchical architecture for microgrids
Distribution network operator (DNO)
Market operator (MO)
Microgrid central controller (MCC)
Local controllers associated with individual DER
F. Katiraei et al, “Microgrids management,” IEEE Power & Energy Magazine, May/June 2008

## Slide 46: Microgrid central controller
F. Katiraei et al, “Microgrids management,” IEEE Power & Energy Magazine, May/June 2008

## Slide 47: Decentralized coordination of microgrids
F. Katiraei et al, “Microgrids management,” IEEE Power & Energy Magazine, May/June 2008

## Slide 48: Protection system for microgrids
Transition between interconnected and islanded mode
Short circuit capacity significantly changes between interconnected and islanded mode. Change in protection settings and logics may be needed.
Fault detection may become an issue because low fault current contribution from power electronic based DERs
Protection coordination should be prepared for bi-directional fault current contributions
Redefinition of anti-islanding protection
  In microgrid anti-islanding protection that shuts down DER is not convenient
  Islanding detection relays can be used to trigger transition between grid connected and islanded operation method

## Slide 49: Extra slides

## Slide 50: Other possible topics to cover
Provision of local blackstart?
Determination of benefits?
Policy?
Communication infrastructure and protocols?

## Slide 51: CERTS tools
Distribution energy resources customer adoption model (DER-CAM) (Lawrence Berkeley National Lab)
Grid Analysis Tool (Grid) (Georgia Institute of Technology)
  All necessary electrical analysis needed to design microgrids. (Unbalanced three-phase, and single phase system, voltage and frequency stability, stray voltages, currents and ground potentials)
  Didn’t find????????????

## Slide 52: Module 10 Concluding Comments
1
2
3
4