## Slide 1: Substation and Distribution Automation
Module 6: Volt-VAR optimization

## Slide 2: Module 6 Overview
Part 1: Traditional Voltage Control
Part 2: Volt-VAR Optimization

## Slide 3: Part 1: Traditional Voltage Control
The voltage supplied to the customer is generally maintained within the limits set by ANCI C84.1, 120V +/-5%.
This is done by setting the voltage at the “head” of the feeder at the high end of the band, to ensure that the voltage drop at peak load does not exceed limits.

## Slide 4: Traditional Voltage Control (Regulators)
Regulators are often installed at the substation in order to adjust the voltage at the head of the feeder.

## Slide 5: Traditional Voltage Control (Regulators)
In extreme cases a down stream voltage regulator can be installed.

## Slide 6: Traditional Voltage Control (Capacitors)
If the feeder is heavily loaded then a shunt capacitor can be installed to raise the voltage.
This also reduces the reactive power needs of the feeder, reducing losses.

## Slide 7: ANCI C84.1
American National Standards Institute (ANSI) C84.1 standard defines operating limits for distribution systems.
Range A (normal steady-state):114V-126V (RMS)
Range B(emergency steady-state):107V-127V (RMS)
<3% voltage unbalance at the utility meter

## Slide 8: Operation of Voltage Control Devices
Voltage control devices, both regulators and shunt capacitors, traditionally have been operated in a stand alone mode.
Operation is achieved through manual operation, local set points, and on occasion remote measurements.
While the set points may be coordinated, it is a static coordination and does not account for time dependant variations in the system behavior.

## Slide 9: Part 2: Volt-VAR Optimization
Volt-VAR Optimization exists in many forms.
The general principle is to control the voltage and reactive power on a distribution feeder so that load can be managed.
  Voltage optimization involves “flattening” the voltage profile and possibly lowering the level.
  VAR optimization involves controlling the flow of reactive power, which has an impact on voltage.

## Slide 10: Volt-VAR Optimization
Voltage Reduction
  When lowering the voltage it is necessary to ensure that the voltage on all points of the system remain within specifications.
  The use of End Of Line (EOL) measurements can help to ensure that voltages at remote points are not too low.
  This is similar to operating a regulator in “REMOTE” except that there can be multiple measurement points.
VAR Optimization
  When capacitors operate based on local readings there is no regard for the rest of the system.
  VAR optimization allows capacitors to work in a coordinate manner to reduce overall reactive power flows, thus reducing system losses.

## Slide 11: Volt-VAR Optimization cont.
There are numerous Volt-VAR optimization options commercially available:
  General Electric: Coordinated Volt-VAR Control
  Cooper: Integrated Volt VAR Control
  ABB: Volt VAR Optimization
  PCS UtiliData: AdaptiVolt
Some support the operation of multiple regulators on a feeder.
There are also numerous academic papers on the topic. We will examine the following method:
  “V. Borozan, M. Baran, and D. Novosel, “Integrated Volt/VAR Control in Distribution Systems”, IEEE PES Winter Meeting, 2001.”

## Slide 12: Volt-VAR Optimization
Borozan, Baran, and Novosel Implementation
  Simple control scheme
  Works for radial feeders
    No “cross branch” optimization – each “regulator branch” handled independently
    No downstream coordination – branches with multiple regulators may have voltage violations while things move
  Two-stage process
    Optimize voltage
    Optimize reactive power

## Slide 13: Volt-VAR Optimization – GridLAB-D
Voltage Optimization
  Determine the minimum voltage
  Determine “state of the system”
  Command regulators
Capacitor Optimization
  Determine reactive power value
  Find next capacitor to switch

## Slide 14: Volt-VAR Optimization – Voltage Steps
Determine minimum voltage in measurements and regulator load-side voltage
Compute voltage drop between regulator and minimum voltage
Apply voltage drop to desired voltage to obtain corrected desired voltage
Ensure corrected desired voltage does not exceed the minimum or maximum ratings of the system

## Slide 15: Volt-VAR Optimization – Voltage Steps (continued)
Determine if in high-loading or low-loading deadband conditions by examining voltage drop
Determine if corrected desired voltage is outside the deadband of current voltage
If tap change, ensure the estimated new voltage will not exceed the minimum and maximum values of the system
If new voltage is acceptable, change taps of regulator

## Slide 16: Volt-VAR Optimization – Capacitor Optimization
Only occurs if no regulator changes are requested
Determine reactive power on line of interest (substation transformer) – compute the current power factor
Determine if power factor is below the desired power factor
If outside range, proceed through capacitors –only change one per operation cycle:
  Capacitor active and reactive power < capacitor size * d_min: switch capacitor to inactive
  Capacitor inactive and reactive power > capacitor size * d_max: switch capacitor to active
  Neither: proceed to next largest capacitor and continue check

## Slide 17: Volt-VAR Optimization – Example
Simple “4-node” system
  Nodes represent measurements
  Two Regulators
  Two Capacitors
  Assume regulators have 100 V tap positions
4700 V end of line desired
0.99 pf desired
Minimize reactive flow through Xfmr

## Slide 18: Volt-VAR Optimization Example – Initial Voltages
Determine minimum voltage and regulator load-side voltages
  Reg 1 – 4850 V and 4600 V
  Reg 2 – 4840 V and 4700 V
1a. Evaluate voltages
  Reg 1 end-of-line voltage is low
  Reg 2 is acceptable

## Slide 19: Volt-VAR Optimization Example – Condition Evaluation
Compute voltage drop between regulator and minimum voltage
  Reg 1 – 250 V
  Reg 2 – No action needed, but 140 V drop

## Slide 20: Volt-VAR Optimization Example – Corrective Actions
Corrected desired voltage for Reg 1 is 4950 V
  (4700 desired + 250 V drop)
  Reg 1 is assumed to have an available position to “tap up”
4950 V is assumed to not violate the upper voltage limit
250 V drop is considered high-loading
  Deadband is assumed to be +/- 1 tap (+/- 100 V)

## Slide 21: Volt-VAR Optimization Example – Corrective Actions (continued)
Outside the deadband of desired voltage
  +1 tap change is desired
New voltage will be 4950 V
  4850 V current + 100 V tap up
  Will not violate upper voltage limit
Value of new voltage acceptable
  Execute tap change

## Slide 22: Volt-VAR Optimization Example – Voltage Result
All voltages at desired values
If Node 3 were still unacceptable, process would repeat
Adjustment could occur simultaneous to Reg 2/Node 4 adjustments

## Slide 23: Volt-VAR Optimization Example – Reactive Power Values
Only occurs once voltage changes have completed
Determine reactive power and compute power factor
  900 kVAr of reactive power
  0.95 power factor
Determine if below desired power factor
  0.99 desired power factor, so is below (action needed)

## Slide 24: Volt-VAR Optimization Example – Reactive Power Correction
Outside range, proceed through capacitors
  Use default d_min of 0.3 and d_max 0f 0.6
  5 MVAr capacitor
    0.3 * 5 MVAr = 1.5 MVAr – too big, no action
  1 MVAr capacitor
    0.3 * 1 MVAr = 0.3 MVAr – under limit, switch it in

## Slide 25: Volt-VAR Optimization Example – Reactive Power Result
Evaluate results
  If no voltage changes are required, proceed
  If more reactive changes required, rescan the capacitor list
Capacitor changes can influence voltages
  May exceed limits
  Can cause regulator and capacitor “fighting” in this simple algorithm

## Slide 26: Integrated Volt/VAR Control in Distribution Systems
This is an openly available Volt-VAR control system that has been implemented in GridLAB-D.
It is composed of 2 coordinated goals.
  Voltage reduction
  VAR control

## Slide 27: Modified IEEE 13 Node System with Volt-VAR Control
EOL Measurements
VAR Controlled Link

## Slide 28: Case 1: Local Voltage Control
Voltage at node:671 is controlled by regulator to 2,400V:
Voltage at node:675 is maintained by capacitors:

## Slide 29: Case 1: Local Voltage Control cont.
Voltage is still operated at an upper level. As a result, there are energy reductions that are not realized.
Power factor is not maintained:

## Slide 30: Case 2: Coordinated Volt/VAR Control
Voltage is regulated at remote nodes 652 and 680, to a values of 2,200V:
Energy consumption is reduced:
Power factor is maintained

## Slide 31: Module 6 Concluding Comments
1
2
3
4